S401 Humidity Transducer

## Product Highlights:

Special seal design for anti acid and dust

High anti poor environment ability

Wide operating temperature range

Standard voltage/current output

Special circuit design, wide measurement range

Accurate and stable

This document applies to S401A, S401B, S401C, S401D, S401E, S401F

## Applications:

## Widely used in food and tobacco processing and storage, large walk in freezer, and industry production sites, as well as any other suitable locations.

Dimensions (mm)

## Specification:

|  | Humidity |
| --- | --- |
| Operating Range | 0%RH ~100%RH |
| Accuracy | <±2%RH (25 oC, 10%RH -90%RH) |
| Long Term Error | <1%RH/year |
| Sensor | Humidity sensitive capacitor |
| temperature | -40 oC ~60 oC |
| storage | -40 oC ~60 oC |
| connection | 3 strand (0.2mm2) |
| Supplied cable length | 1.5m |
| Housing Material | ABS plastic |

- Input signal and power supply:

|  | S401A | S401B | S401C | S401D | S401E | S401F | Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Output Signal | 4 mA – 20mA | 0 mA -10mA | 0 mA -20mA | 0 V -10V | 0 V -5V | 0 V -1V |  |
| Power Supply | 12 V -24V | 12 V -24V | 12 V -24V | 18 V -24V | 12 V -24V | 5V/7V -24V | DC |
| Supply Current | <25mA | <15mA | <25mA | <15mA | <15mA | <2mA/15mA |  |
| Input Resistance | <500ohm | <500ohm | <500ohm |  |  |  |  |
| Load Resistance |  |  |  | >10k | >10k | >10k |  |

- Relation between output signal and operating range        Relation between Accuracy and operating range

- Installation:

- Note: pointing the sensor downward will help the accuracy.

Model number

S401    X

Output signal

A:  4-20mA         D:  0-10V

B:  0-10mA         E:  0-5V

C:  0-20mA         F:  0-1V

- Connection

S401A:   2 wire current transducer

Yellow

Red

white

Relation between DC supply U and the sampling

resistence Rs:  28V>U>7V+Imax* Rs

Where  Imax=20mA

S401B/C:   3 wire current transducer

Yellow

Red

white

Relation between DC supply U and the sampling

resistence Rs:  28V>U>7V+Imax* Rs

红

where   Imax=10mA  (B type)

or 	 Imax=20mA  (C type)

S401D/E/F:  Voltage transducer

Yellow

Red

white

RL is the load resistor

- U is the DC supply